## Pipe Sizing Calc
Density(Kg/m^3) | Dynamic Viscosity (Kg/(m*s)) | Discharge Q (m^3/s) | Optimised Velocity m/s | PE100 Pipe roughness Ks (mm) | Link to find the colebook white friction factor
1000 | 0.001002 | 0.3125 | 1.5 | 0.0015 | https://www.pe100plus.com/PE-Pipes/Technical-guidance/Trenchless/Methods/PE-Pipe-i1341.html
Link for Maximum Velocity in pipes
https://www.engineeringtoolbox.com/flow-velocity-water-pipes-d_385.html
PE100 (PN10) |  |  |  |  | Available Diamter PE100
Available Diameter Pipe (mm) | Thickness of pipe | Inner Diameter of Pipe (mm) | Effective surface area (m^2) | Water velocity (m/s) | https://www.radius-systems.com/storage/app/media/Downloads/Polyethylene%20pipes%20for%20all%20applications.pdf
225 | 13.4 | 198.2 | 0.030837 | 10.1338
250 | 14.8 | 220.4 | 0.038132 | 8.1952 | PE100 Pipe : UK Manufacture
280 | 16.6 | 246.8 | 0.047815 | 6.5357 | http://www.welbrit.co.uk/polyethylene.php
315 | 18.7 | 277.6 | 0.060493 | 5.1658
355 | 21.2 | 312.6 | 0.076709 | 4.0738 | PE100 internal rougness (mm)
400 | 23.7 | 352.6 | 0.097597 | 3.202 | https://www.pipeflow.com/pipe-pressure-drop-calculations/pipe-roughness
450 | 26.7 | 396.6 | 0.12347 | 2.5309
500 | 29.7 | 440.6 | 0.15239 | 2.0506
560 | 33.2 | 493.6 | 0.19126 | 1.6339
630 | 37.4 | 555.2 | 0.24197 | 1.2915
710 | 42.1 | 625.8 | 0.30743 | 1.0165
800 | 47.4 | 705.2 | 0.39039 | 0.80049
900 | 53.3 | 793.4 | 0.49414 | 0.63241
1000 | 59.3 | 881.4 | 0.60984 | 0.51243
Inner Diameter of Pipe (mm) | Reynold's number | Moody friction factor | Barr friction factor
493.5 | 738772.4551 | 0.0073784 | 0.0123
555.2 | 831137.7246 | 0.0072147 | 0.012087
Moody |  | Barr
| Gradient i_moody |  | Gradient i_barr
| 0.0017146 |  | 0.0028583
| 0.0014902 |  | 0.0024966
PE100 (PN16)
Available Diameter Pipe (mm) | Thickness of pipe | Inner Diameter of Pipe (mm) | Effective surface area (m^2) | Water velocity (m/s)
225 | 20.3 | 184.4 | 0.026693 | 11.7073
250 | 22.7 | 204.6 | 0.032861 | 9.5098
280 | 25.4 | 229.2 | 0.041238 | 7.5779
315 | 28.6 | 257.8 | 0.052172 | 5.9898
355 | 32.2 | 290.6 | 0.066292 | 4.714
400 | 36.3 | 327.4 | 0.084145 | 3.7138
450 | 40.9 | 368.2 | 0.10642 | 2.9364
500 | 45.4 | 409.2 | 0.13144 | 2.3774
560 | 50.8 | 458.4 | 0.16495 | 1.8945
630 | 57.2 | 515.6 | 0.20869 | 1.4975
710 | 64.5 | 581 | 0.26499 | 1.1793
Inner Diameter of Pipe (mm) | Reynold's number | Moody friction factor | Barr friction factor
515.6 | 771856.2874 | 0.0073162 | 0.012241
581 | 869760.479 | 0.0071547 | 0.011994
Moody |  | Barr
| Gradient i_moody |  | Gradient i_barr
| 0.0016272 |  | 0.0027227
| 0.0014122 |  | 0.0023674

## Pump Sizing Calc
PE PN16 630mm
PUMP 1 | Inner Diameter (mm) | Area (m^2) | Length L (m) | PE100 Pipe roughness Ks (mm) | Dynamic Viscosity (Kg/(m*s)) | Theoretical Duty Point Flowrate Q (L/s) | Barr Formula friction factor
| 515.6 | 0.20869 | 20264.4583 | 0.0015 | 0.001002 | 312.5 | 0.012241
Flowrate Q (L/s) | Water velocity u (m/s) | Reynold's Number | Friction factro (Barr) | I Gradient | Head (m) | Duty Point Flowrate (L/s)
0 | 0 | 0 | 0 | 0 | 44.88 | 312.5 |  | Pump Search Tool
40 | 0.19167 | 98630.1524 | 0.017935 | 6.5137e-05 | 45.7809 | 312.5 |  | https://www.xylect.com/bin/Xylect.dll?IS__NEXTPAGE=startup&IS__NEXTPAGE=BDYHOME&IS__AREA=GREAT%20BRITAIN&IS__COUNTRY=UNITED%20KINGDOM&IS__BROWSER=%23%23%231584%23821
80 | 0.38335 | 197260.3049 | 0.015626 | 0.00026055 | 48.4836 | 312.5
120 | 0.57502 | 295890.4573 | 0.01448 | 0.00058623 | 52.9881 | 312.5
160 | 0.7667 | 394520.6098 | 0.013745 | 0.0010422 | 59.2944 | 312.5
200 | 0.95837 | 493150.7622 | 0.013213 | 0.0016284 | 67.4025 | 312.5 |  | 10% larger than the duty point flowrate
240 | 1.15 | 591780.9147 | 0.012803 | 0.0023449 | 77.3124 | 312.5
280 | 1.3417 | 690411.0671 | 0.012472 | 0.0031917 | 89.0241 | 312.5 |  | 1st pump station valves:
320 | 1.5334 | 789041.2195 | 0.012196 | 0.0041688 | 102.5375 | 312.5 |  | non return valve,
360 | 1.7251 | 887671.372 | 0.011961 | 0.0052761 | 117.8528 | 312.5
400 | 1.9167 | 986301.5244 | 0.011758 | 0.0065137 | 134.9699 | 312.5 |  | Pressure instrument for controlling the pressure along the pipes
440 | 2.1084 | 1084931.6769 | 0.011578 | 0.0078815 | 153.8888 | 312.5
480 | 2.3001 | 1183561.8293 | 0.011418 | 0.0093797 | 174.6095 | 312.5
520 | 2.4918 | 1282191.9818 | 0.011274 | 0.011008 | 197.1319 | 312.5
560 | 2.6834 | 1380822.1342 | 0.011144 | 0.012767 | 221.4562 | 312.5
600 | 2.8751 | 1479452.2866 | 0.011025 | 0.014656 | 247.5823 | 312.5
640 | 3.0668 | 1578082.4391 | 0.010916 | 0.016675 | 275.5101 | 312.5
Manufacture Datasheet:
| Q (l/s) | Head (m)
400 | 111.1111 | 130
500 | 138.8889 | 129
600 | 166.6667 | 127
700 | 194.4444 | 125
800 | 222.2222 | 123
900 | 250 | 120
1000 | 277.7778 | 118
1100 | 305.5556 | 115
1200 | 333.3333 | 110
1300 | 361.1111 | 105
1350 | 375 | 100
PUMP 2
Length (m)
9781.3406
Flowrate Q (L/s) | Water velocity u (m/s) | Reynold's Number | Friction factro (Barr) | I Gradient | Head (m) | Duty Point Flowrate (L/s)
0 | 0 | 0 | 0 | 0 | 24.21 | 312.5
40 | 0.19167 | 98630.1524 | 0.017935 | 6.5137e-05 | 24.6504 | 312.5
80 | 0.38335 | 197260.3049 | 0.015626 | 0.00026055 | 25.9718 | 312.5
120 | 0.57502 | 295890.4573 | 0.01448 | 0.00058623 | 28.174 | 312.5
160 | 0.7667 | 394520.6098 | 0.013745 | 0.0010422 | 31.2571 | 312.5
200 | 0.95837 | 493150.7622 | 0.013213 | 0.0016284 | 35.2211 | 312.5
240 | 1.15 | 591780.9147 | 0.012803 | 0.0023449 | 40.0659 | 312.5
280 | 1.3417 | 690411.0671 | 0.012472 | 0.0031917 | 45.7917 | 312.5
320 | 1.5334 | 789041.2195 | 0.012196 | 0.0041688 | 52.3983 | 312.5
360 | 1.7251 | 887671.372 | 0.011961 | 0.0052761 | 59.8859 | 312.5
400 | 1.9167 | 986301.5244 | 0.011758 | 0.0065137 | 68.2543 | 312.5
440 | 2.1084 | 1084931.6769 | 0.011578 | 0.0078815 | 77.5036 | 312.5
480 | 2.3001 | 1183561.8293 | 0.011418 | 0.0093797 | 87.6338 | 312.5
520 | 2.4918 | 1282191.9818 | 0.011274 | 0.011008 | 98.6448 | 312.5
560 | 2.6834 | 1380822.1342 | 0.011144 | 0.012767 | 110.5368 | 312.5
600 | 2.8751 | 1479452.2866 | 0.011025 | 0.014656 | 123.3097 | 312.5
640 | 3.0668 | 1578082.4391 | 0.010916 | 0.016675 | 136.9634 | 312.5
Manufacture Datasheet:
| Q (l/s) | Head (m)
400 | 111.1111 | 64
500 | 138.8889 | 63
600 | 166.6667 | 62
700 | 194.4444 | 61
800 | 222.2222 | 60
900 | 250 | 58
1000 | 277.7778 | 56
1100 | 305.5556 | 54
1200 | 333.3333 | 51
1300 | 361.1111 | 49
1400 | 388.8889 | 48
PUMP 3
Length (m)
9826.6133
Flowrate Q (L/s) | Water velocity u (m/s) | Reynold's Number | Friction factro (Barr) | I Gradient | Head (m) | Duty Point Flowrate (L/s)
0 | 0 | 0 | 0 | 0 | 16.59 | 312.5
40 | 0.19167 | 98630.1524 | 0.017935 | 6.5137e-05 | 17.0325 | 312.5
80 | 0.38335 | 197260.3049 | 0.015626 | 0.00026055 | 18.3599 | 312.5
120 | 0.57502 | 295890.4573 | 0.01448 | 0.00058623 | 20.5723 | 312.5
160 | 0.7667 | 394520.6098 | 0.013745 | 0.0010422 | 23.6697 | 312.5
200 | 0.95837 | 493150.7622 | 0.013213 | 0.0016284 | 27.652 | 312.5
240 | 1.15 | 591780.9147 | 0.012803 | 0.0023449 | 32.5193 | 312.5
280 | 1.3417 | 690411.0671 | 0.012472 | 0.0031917 | 38.2716 | 312.5
320 | 1.5334 | 789041.2195 | 0.012196 | 0.0041688 | 44.9088 | 312.5
360 | 1.7251 | 887671.372 | 0.011961 | 0.0052761 | 52.431 | 312.5
400 | 1.9167 | 986301.5244 | 0.011758 | 0.0065137 | 60.8381 | 312.5
440 | 2.1084 | 1084931.6769 | 0.011578 | 0.0078815 | 70.1303 | 312.5
480 | 2.3001 | 1183561.8293 | 0.011418 | 0.0093797 | 80.3073 | 312.5
520 | 2.4918 | 1282191.9818 | 0.011274 | 0.011008 | 91.3694 | 312.5
560 | 2.6834 | 1380822.1342 | 0.011144 | 0.012767 | 103.3164 | 312.5
600 | 2.8751 | 1479452.2866 | 0.011025 | 0.014656 | 116.1483 | 312.5
640 | 3.0668 | 1578082.4391 | 0.010916 | 0.016675 | 129.8653 | 312.5
Manufacture Datasheet:
| Q (l/s) | Head (m)
400 | 111.1111 | 57
500 | 138.8889 | 56
600 | 166.6667 | 55
700 | 194.4444 | 54
800 | 222.2222 | 53
900 | 250 | 52
1000 | 277.7778 | 49
1100 | 305.5556 | 48
1200 | 333.3333 | 46
1300 | 361.1111 | 42
1400 | 388.8889 | 38

## MAIN ROUTE
latitude | longitude | altitude (m) | X | Y | Distance (km)
57.5499 | -2.437 | 98.4 | 1.0044 | -0.042534 | 0
57.5475 | -2.4374 | 101 | 1.0044 | -0.04254 | 0.2675
57.5459 | -2.4372 | 103.5 | 1.0044 | -0.042537 | 0.44818
57.5439 | -2.4361 | 105.9 | 1.0043 | -0.042519 | 0.67799
57.5399 | -2.4338 | 88.3 | 1.0043 | -0.042477 | 1.1491
57.5371 | -2.4335 | 66.3 | 1.0042 | -0.042472 | 1.4556
57.5319 | -2.4332 | 52 | 1.0041 | -0.042468 | 2.0324
57.5278 | -2.4331 | 50.1 | 1.004 | -0.042465 | 2.4981
57.5233 | -2.4302 | 46 | 1.004 | -0.042415 | 3.0216
57.5167 | -2.4279 | 49 | 1.0039 | -0.042375 | 3.7735
57.5117 | -2.4251 | 58.9 | 1.0038 | -0.042327 | 4.3501
57.5058 | -2.4221 | 64 | 1.0037 | -0.042274 | 5.0273
57.5037 | -2.4217 | 60.5 | 1.0036 | -0.042266 | 5.2606
57.5022 | -2.4218 | 58 | 1.0036 | -0.042269 | 5.4306
57.4993 | -2.4227 | 56 | 1.0036 | -0.042284 | 5.7535
57.4976 | -2.4232 | 56.1 | 1.0035 | -0.042293 | 5.9491
57.4932 | -2.4242 | 58.8 | 1.0034 | -0.042309 | 6.4435
57.492 | -2.424 | 54 | 1.0034 | -0.042307 | 6.5741
57.4877 | -2.4255 | 53 | 1.0033 | -0.042333 | 7.0671
57.4833 | -2.4272 | 55.2 | 1.0033 | -0.042362 | 7.5654
57.4819 | -2.4269 | 59 | 1.0032 | -0.042358 | 7.715
57.4805 | -2.4254 | 61 | 1.0032 | -0.042331 | 7.9018
57.478 | -2.4234 | 57.2 | 1.0032 | -0.042296 | 8.2006
57.4749 | -2.4224 | 57.3 | 1.0031 | -0.042278 | 8.5468
57.4721 | -2.4208 | 56.2 | 1.0031 | -0.04225 | 8.8804
57.47 | -2.4194 | 58 | 1.003 | -0.042226 | 9.1247
57.4671 | -2.417 | 56.6 | 1.003 | -0.042185 | 9.482
57.4646 | -2.4152 | 55.2 | 1.0029 | -0.042153 | 9.7789
57.4623 | -2.4118 | 54.8 | 1.0029 | -0.042093 | 10.106
57.4594 | -2.4068 | 52.6 | 1.0029 | -0.042006 | 10.5429
57.4537 | -2.4 | 52.8 | 1.0028 | -0.041888 | 11.3001
57.4523 | -2.399 | 51.1 | 1.0027 | -0.04187 | 11.4623
57.4503 | -2.3988 | 53.6 | 1.0027 | -0.041868 | 11.687
57.4424 | -2.403 | 69.1 | 1.0026 | -0.04194 | 12.5988
57.4381 | -2.4043 | 63.4 | 1.0025 | -0.041963 | 13.0794
57.437 | -2.4043 | 61.3 | 1.0025 | -0.041964 | 13.2035
57.4322 | -2.4034 | 57.2 | 1.0024 | -0.041948 | 13.7375
57.4301 | -2.402 | 65 | 1.0023 | -0.041923 | 13.9876
57.4262 | -2.3931 | 52.6 | 1.0023 | -0.041767 | 14.6786
57.423 | -2.3839 | 52.7 | 1.0022 | -0.041607 | 15.3306
57.42 | -2.3734 | 83.6 | 1.0022 | -0.041423 | 16.0466
57.4147 | -2.371 | 106.8 | 1.0021 | -0.041382 | 16.6509
57.4121 | -2.3666 | 113.7 | 1.002 | -0.041305 | 17.0408
57.4045 | -2.3664 | 133.5 | 1.0019 | -0.041302 | 17.885
57.4004 | -2.3626 | 136.4 | 1.0018 | -0.041235 | 18.4002
57.3938 | -2.3581 | 131.7 | 1.0017 | -0.041156 | 19.1834
57.3852 | -2.3495 | 140.6 | 1.0016 | -0.041007 | 20.2645
57.3756 | -2.3385 | 172.2 | 1.0014 | -0.040815 | 21.5197
57.3716 | -2.3348 | 173 | 1.0013 | -0.04075 | 22.0213
57.3586 | -2.3308 | 150 | 1.0011 | -0.040681 | 23.4865
57.353 | -2.3292 | 156.6 | 1.001 | -0.040652 | 24.116
57.3434 | -2.332 | 120.7 | 1.0008 | -0.040701 | 25.1915
57.3359 | -2.3353 | 87 | 1.0007 | -0.040758 | 26.0489
57.3268 | -2.3388 | 93.3 | 1.0005 | -0.040821 | 27.0804
57.3197 | -2.3459 | 91.9 | 1.0004 | -0.040943 | 27.9789
57.3116 | -2.3501 | 100.3 | 1.0003 | -0.041017 | 28.9201
57.3073 | -2.3487 | 125.8 | 1.0002 | -0.040992 | 29.4052
57.301 | -2.3468 | 142 | 1.0001 | -0.04096 | 30.108
57.29 | -2.351 | 106.1 | 0.9999 | -0.041033 | 31.3579
57.2802 | -2.349 | 68.2 | 0.99973 | -0.040998 | 32.4597
57.2695 | -2.3448 | 94.3 | 0.99954 | -0.040925 | 33.674
57.2607 | -2.3406 | 100.5 | 0.99939 | -0.040851 | 34.6878
57.253 | -2.3377 | 68.9 | 0.99925 | -0.0408 | 35.5595
57.2436 | -2.3316 | 65.3 | 0.99909 | -0.040694 | 36.662
57.2333 | -2.3322 | 47 | 0.99891 | -0.040704 | 37.8062
57.2213 | -2.3316 | 65.4 | 0.9987 | -0.040694 | 39.1425
57.2138 | -2.3366 | 87.3 | 0.99857 | -0.040781 | 40.0368
57.2128 | -2.3371 | 81 | 0.99855 | -0.04079 | 40.1495
57.2066 | -2.3346 | 82.7 | 0.99844 | -0.040746 | 40.8515
57.2 | -2.3323 | 94.1 | 0.99833 | -0.040707 | 41.6037
57.1962 | -2.3311 | 104.6 | 0.99826 | -0.040686 | 42.0245
57.1891 | -2.3293 | 140.6 | 0.99814 | -0.040654 | 42.8226
57.1843 | -2.3244 | 140.5 | 0.99805 | -0.040569 | 43.4339
57.1794 | -2.3197 | 186.2 | 0.99797 | -0.040487 | 44.0458
57.1761 | -2.3179 | 187.7 | 0.99791 | -0.040454 | 44.4373
57.1717 | -2.3165 | 176.8 | 0.99783 | -0.040431 | 44.9262
57.1667 | -2.3126 | 162.6 | 0.99775 | -0.040363 | 45.5308
57.1649 | -2.3049 | 209 | 0.99772 | -0.040228 | 46.0396
57.1635 | -2.3017 | 193.1 | 0.99769 | -0.040173 | 46.2846
PN10 (560mm) |  |  |  |  | PN 16 (630 mm)
|  | Gradient Line |  |  |  |  | Gradient Line
Gradient i_moody | Maximum Pipe Head (m) | Pump 50 head |  |  | Gradient i_moody | Maximum Pipe Head (m) | Pump 100 head
0.00171 | 198.4 | 148.4 |  |  | 0.00163 | 258.4 | 198.4
| 201 | 147.9426 |  |  |  | 261 | 197.964
| 203.5 | 147.6336 |  |  |  | 263.5 | 197.6695
| 205.9 | 147.2406 |  |  |  | 265.9 | 197.2949
| 188.3 | 146.435 |  |  |  | 248.3 | 196.5269
| 166.3 | 145.9109 |  |  |  | 226.3 | 196.0273
| 152 | 144.9246 |  |  |  | 212 | 195.0872
| 150.1 | 144.1283 |  |  |  | 210.1 | 194.3281
| 146 | 143.2331 |  |  |  | 206 | 193.4749
| 149 | 141.9474 |  |  |  | 209 | 192.2493
| 158.9 | 140.9613 |  |  |  | 218.9 | 191.3093
| 164 | 139.8034 |  |  |  | 224 | 190.2056
| 160.5 | 139.4043 |  |  |  | 220.5 | 189.8252
| 158 | 139.1137 |  |  |  | 218 | 189.5481
| 156 | 138.5615 |  |  |  | 216 | 189.0218
| 156.1 | 138.227 |  |  |  | 216.1 | 188.703
| 158.8 | 137.3817 |  |  |  | 218.8 | 187.8972
| 154 | 137.1583 |  |  |  | 214 | 187.6843
| 153 | 136.3153 |  |  |  | 213 | 186.8807
| 155.2 | 135.4631 |  |  |  | 215.2 | 186.0683
| 159 | 135.2073 |  |  |  | 219 | 185.8245
| 161 | 134.8879 |  |  |  | 221 | 185.5201
| 157.2 | 134.377 |  |  |  | 217.2 | 185.0331
| 157.3 | 133.785 |  |  |  | 217.3 | 184.4688
| 156.2 | 133.2144 |  |  |  | 216.2 | 183.9249
| 158 | 132.7968 |  |  |  | 218 | 183.5268
| 156.6 | 132.1858 |  |  |  | 216.6 | 182.9444
| 155.2 | 131.6781 |  |  |  | 215.2 | 182.4604
| 154.8 | 131.1188 |  |  |  | 214.8 | 181.9273
| 152.6 | 130.3717 |  |  |  | 212.6 | 181.2151
| 152.8 | 129.0768 |  |  |  | 212.8 | 179.9808
| 151.1 | 128.7994 |  |  |  | 211.1 | 179.7164
| 153.6 | 128.4152 |  |  |  | 213.6 | 179.3502
| 169.1 | 126.856 |  |  |  | 229.1 | 177.8639
| 163.4 | 126.0342 |  |  |  | 223.4 | 177.0805
| 161.3 | 125.8221 |  |  |  | 221.3 | 176.8784
| 157.2 | 124.9089 |  |  |  | 217.2 | 176.0079
| 165 | 124.4813 |  |  |  | 225 | 175.6003
| 152.6 | 123.2996 |  |  |  | 212.6 | 174.4739
| 152.7 | 122.1847 |  |  |  | 212.7 | 173.4112
| 183.6 | 120.9603 |  |  |  | 243.6 | 172.2441
| 206.8 | 119.9269 | Pump 60 head |  |  | 266.8 | 171.259
| 213.7 | 119.2602 | 179.2602 |  |  | 273.7 | 170.6234
| 233.5 |  | 178.8027 |  |  | 293.5 | 169.2474
| 236.4 |  | 178.4938 |  |  | 296.4 | 168.4076
| 231.7 |  | 178.1008 |  |  | 291.7 | 167.131
| 240.6 |  | 177.2952 |  |  | 300.6 | 165.3689 | Pump 50 head
| 272.2 |  | 176.771 |  |  | 332.2 | 163.323 | 193.323
| 273 |  | 175.7848 |  |  | 333 |  | 192.8869
| 250 |  | 174.9885 |  |  | 310 |  | 192.5924
| 256.6 |  | 174.0933 |  |  | 316.6 |  | 192.2178
| 220.7 |  | 172.8076 |  |  | 280.7 |  | 191.4499
| 187 |  | 171.8215 |  |  | 247 |  | 190.9503
| 193.3 |  | 170.6636 |  |  | 253.3 |  | 190.0101
| 191.9 |  | 170.2645 |  |  | 251.9 |  | 189.2511
| 200.3 |  | 169.9739 |  |  | 260.3 |  | 188.3978
| 225.8 |  | 169.4217 |  |  | 285.8 |  | 187.1722
| 242 |  | 169.0872 |  |  | 302 |  | 186.2323
| 206.1 |  | 168.2419 |  |  | 266.1 |  | 185.1285
| 168.2 |  | 168.0185 |  |  | 228.2 |  | 184.7481
| 194.3 |  | 167.1755 |  |  | 254.3 |  | 184.4711
| 200.5 |  | 166.3233 |  |  | 260.5 |  | 183.9447
| 168.9 |  | 166.0675 |  |  | 228.9 |  | 183.6259
| 165.3 |  | 165.7481 |  |  | 225.3 |  | 182.8201
| 147 |  | 165.2372 |  |  | 207 |  | 182.6072
| 165.4 |  | 164.6452 |  |  | 225.4 |  | 181.8037
| 187.3 |  | 164.0746 |  |  | 247.3 |  | 180.9913
| 181 |  | 163.657 |  |  | 241 |  | 180.7475
| 182.7 |  | 163.046 |  |  | 242.7 |  | 180.443
| 194.1 |  | 162.5383 |  |  | 254.1 |  | 179.956
| 204.6 |  | 161.979 |  |  | 264.6 |  | 179.3917
| 240.6 |  | 161.2319 | Pump 60 head |  | 300.6 |  | 178.8478
| 240.5 |  | 159.937 | 219.937 |  | 300.5 |  | 178.4497
| 286.2 |  |  | 219.4795 |  | 346.2 |  | 177.8674
| 287.7 |  |  | 219.1706 |  | 347.7 |  | 177.3834
| 276.8 |  |  | 218.7776 |  | 336.8 |  | 176.8502
| 262.6 |  |  | 217.972 |  | 322.6 |  | 176.1381 | Pump 20 head
| 309 |  |  | 217.4478 |  | 369 |  | 174.9038 | 194.9038
| 293.1 |  |  | 216.4616 |  | 353.1 |  |  | 194.4677
PN10 (560 mm) |  |  |  |  | PN 16 (630 mm)
| Gradient Line |  |  |  |  | Gradient Line
Gradient i_barr | Pump 50 head |  |  |  | Gradient i_barr | Pump 100 head
0.002858 | 148.4 |  |  |  | 0.00272 | 198.4
| 147.6355 |  |  |  |  | 197.6724
| 147.1191 |  |  |  |  | 197.181
| 146.4623 |  |  |  |  | 196.5559
| 145.1158 |  |  |  |  | 195.2744
| 144.2398 |  |  |  |  | 194.4407
| 142.5914 |  |  |  |  | 192.8719
| 141.2605 |  |  |  |  | 191.6052
| 139.7644 |  |  |  |  | 190.1814
| 137.6155 |  |  |  |  | 188.1362
| 135.9674 |  |  |  |  | 186.5677
| 134.0321 |  |  |  |  | 184.7258
| 133.3651 |  |  |  |  | 184.0911
| 132.8794 |  |  |  |  | 183.6288
| 131.9564 |  |  |  |  | 182.7504
| 131.3975 |  |  |  |  | 182.2185
| 129.9846 |  |  |  |  | 180.8738
| 129.6113 |  |  |  |  | 180.5185
| 128.2024 |  |  |  |  | 179.1776
| 126.778 |  |  |  |  | 177.822
| 126.3505 |  |  |  |  | 177.4151
| 125.8167 |  |  |  |  | 176.9071
| 124.9627 |  |  |  |  | 176.0944
| 123.9733 |  |  |  |  | 175.1528
| 123.0197 |  |  |  |  | 174.2452
| 122.3216 |  |  |  |  | 173.5808
| 121.3006 |  |  |  |  | 172.6091
| 120.4519 |  |  |  |  | 171.8014
| 119.5172 |  |  |  |  | 170.9118
| 118.2685 |  |  |  |  | 169.7234
| 116.1043 |  |  |  |  | 167.6637
| 115.6407 |  |  |  |  | 167.2225
| 114.9985 |  |  |  |  | 166.6113
| 112.3926 |  |  |  |  | 164.1313
| 111.0189 |  |  |  |  | 162.8239
| 110.6645 |  |  |  |  | 162.4866
| 109.1382 |  |  |  |  | 161.034
| 108.4236 |  |  |  |  | 160.3539
| 106.4486 |  |  |  |  | 158.4742
| 104.5852 |  |  |  |  | 156.7009
| 102.5389 | Pump 80 Head |  |  |  | 154.7533
| 100.8116 | 180.8116 |  |  |  | 153.1095
|  | 180.0471 |  |  |  | 152.0489
|  | 179.5307 |  |  |  | 149.7527
|  | 178.8739 |  |  |  | 148.3514
|  | 177.5275 |  |  |  | 146.221 | Pump 50 Head
|  | 176.6514 |  |  |  | 143.2807 | 193.2807
|  | 175.003 |  |  |  |  | 192.5531
|  | 173.6721 |  |  |  |  | 192.0616
|  | 172.176 |  |  |  |  | 191.4365
|  | 170.0271 |  |  |  |  | 190.1551
|  | 168.379 |  |  |  |  | 189.3213
|  | 166.4437 |  |  |  |  | 187.7525
|  | 165.7767 |  |  |  |  | 186.4859
|  | 165.291 |  |  |  |  | 185.062
|  | 164.3681 |  |  |  |  | 183.0169
|  | 163.8091 |  |  |  |  | 181.4483
|  | 162.3962 |  |  |  |  | 179.6065
|  | 162.023 |  |  |  |  | 178.9717
|  | 160.614 |  |  |  |  | 178.5095
|  | 159.1896 |  |  |  |  | 177.6311
|  | 158.7621 |  |  |  |  | 177.0991
|  | 158.2283 |  |  |  |  | 175.7545
|  | 157.3744 |  |  |  |  | 175.3992
|  | 156.385 |  |  |  |  | 174.0583
|  | 155.4313 |  |  |  |  | 172.7027
|  | 154.7333 |  |  |  |  | 172.2958
|  | 153.7122 |  |  |  |  | 171.7878
|  | 152.8636 |  |  |  |  | 170.9751
|  | 151.9288 |  |  |  |  | 170.0335
|  | 150.6801 |  |  |  |  | 169.1259
|  | 148.5159 |  |  |  |  | 168.4615
[7 empty] | 167.4897 | Pump 45 Head
212.4897
211.7621
211.2707
210.6456
209.3641

## Carbon Footprint
Pipe | [7 empty] | Total distance (m) | Total mass (kg) | Total mass in tonnes (t) | Capital carbon Factor of HDPE | HDPE Density (kg/m3) | Water Density(Kg/m^3) | Water Dynamic Viscosity (Kg/(m*s)) | Discharge Q (m^3/s) | PE100 Pipe roughness Ks (mm)
Required number of PE100 pipes | [7 empty] | 46285 | 4732641.25 | 4732.6412 | 2.52 | 970 | 1000 | 0.001002 | 0.3125 | 0.0015
3857.05
[8 empty] | Outer Diameter (mm) | Thickness | Inner Diameter(mm) | Inner Pipe area (m2) | Outer Pipe Area (m2) | Volume (m3) | Total mass (kg) | Capital Carbon (tonnes)
Total weight of the required pipes
3908734.47 | [7 empty] | 225 | 20.3 | 184.4 | 0.026693 | 0.039741 | 603.9261 | 585808.3139 | 1476.237
[8 empty] | 250 | 22.7 | 204.6 | 0.032861 | 0.049063 | 749.8859 | 727389.3588 | 1833.0212
[8 empty] | 280 | 25.4 | 229.2 | 0.041238 | 0.061544 | 939.8575 | 911661.8184 | 2297.3878
HDPE Approximated carbon footprint (High Density Polythene) | [7 empty] | 315 | 28.6 | 257.8 | 0.052172 | 0.077892 | 1190.444 | 1154730.6599 | 2909.9213
https://lutpub.lut.fi/handle/10024/163642 | [7 empty] | 355 | 32.2 | 290.6 | 0.066292 | 0.09893 | 1510.6342 | 1465315.1781 | 3692.5942
[8 empty] | 400 | 36.3 | 327.4 | 0.084145 | 0.1256 | 1918.7564 | 1861193.7115 | 4690.2082
[8 empty] | 450 | 40.9 | 368.2 | 0.10642 | 0.15896 | 2431.7712 | 2358818.0256 | 5944.2214
[8 empty] | 500 | 45.4 | 409.2 | 0.13144 | 0.19625 | 2999.5437 | 2909557.4351 | 7332.0847
[8 empty] | 560 | 50.8 | 458.4 | 0.16495 | 0.24618 | 3759.4302 | 3646647.2735 | 9189.5511
[8 empty] | 630 | 57.2 | 515.6 | 0.20869 | 0.31157 | 4761.7759 | 4618922.6397 | 11639.6851
[8 empty] | 710 | 64.5 | 581 | 0.26499 | 0.39572 | 6050.9822 | 5869452.7609 | 14791.021
Pumps
Pump 100m head | [7 empty] | velocity (m3/s) | Reynold's Number | Friction factor | Head loss (m) | Pump Power (kW/yr) | Operation Carbon (tonnes) | How many years? | Total carbon
Lowara - e-XC150-280/2500W/L25BDS4AG | [13 empty] | 25
[8 empty] | 11.7073 | 11683.9801 | 0.030633 | 53713.7959 | 203276551.1741 | 18498.1662 | 462454.1539 | 463930.3909
Pump 50m head | [7 empty] | 9.5098 | 9490.7686 | 0.032284 | 33663.4865 | 127397390.6628 | 11593.1626 | 289829.0638 | 291662.0849
[8 empty] | 7.5779 | 7562.814 | 0.03424 | 20237.7127 | 76588376.9625 | 6969.5423 | 174238.5576 | 176535.9454
[8 empty] | 5.9898 | 5977.8748 | 0.036445 | 11965.3472 | 45282119.4634 | 4120.6729 | 103016.8218 | 105926.743
Pump 40m head | [7 empty] | 4.714 | 4704.5861 | 0.038892 | 7015.8399 | 26551014.0165 | 2416.1423 | 60403.5569 | 64096.1511
[8 empty] | 3.7138 | 3706.4257 | 0.041543 | 4128.6785 | 15624729.3277 | 1421.8504 | 35546.2592 | 40236.4674
| Material/Product | Input Unit | Material Type | Carbon Factor | Carbon Factor Units | Conversion Factor | Methodology | 2.9364 | 2930.5226 | 0.044382 | 2451.8285 | 9278793.9164 | 844.3702 | 21109.2562 | 27053.4776
Plastic pipework (HDPE) | 150mm diameter | metres | Plastic | 2.52 | tCO2e/t | 0.0023617 | Carbon factor taken directly from the ICE V3: Plastic > HDPE Pipe. Conversion factor calculated from approximate 150mm pipe wall thickness of 5mm and HDPE density 0.97 t/m3. | 2.3774 | 2372.6921 | 0.04714 | 1536.071 | 5813166.1451 | 528.9981 | 13224.953 | 20557.0377
| 225mm diameter | metres | Plastic | 2.52 | tCO2e/t | 0.0042236 | Carbon factor taken directly from the ICE V3: Plastic > HDPE Pipe. Conversion factor calculated from approximate 225mm pipe wall thickness of 6mm and HDPE density 0.97 t/m3. | 1.8945 | 1890.7035 | 0.050339 | 929.7859 | 3518717.521 | 320.2033 | 8005.0824 | 17194.6335
| 300mm diameter | metres | Plastic | 2.52 | tCO2e/t | 0.0075087 | Carbon factor taken directly from the ICE V3: Plastic > HDPE Pipe. Conversion factor calculated from approximate 300mm pipe wall thickness of 8mm and HDPE density 0.97 t/m3. | 1.4975 | 1494.4687 | 0.053926 | 553.2696 | 2093814.7957 | 190.5371 | 4763.4287 | 16403.1137
| 450mm diameter | metres | Plastic | 2.52 | tCO2e/t | 0.011165 | Carbon factor taken directly from the ICE V3: Plastic > HDPE Pipe. Conversion factor calculated from approximate 450mm pipe wall thickness of 8mm and HDPE density 0.97 t/m3. | 1.1793 | 1176.9564 | 0.057877 | 326.8317 | 1236874.4178 | 112.5556 | 2813.8893 | 17604.9103
| 600mm diameter | metres | Plastic | 2.52 | tCO2e/t | 0.020481 | Carbon factor taken directly from the ICE V3: Plastic > HDPE Pipe. Conversion factor calculated from approximate 600mm pipe wall thickness of 11mm and HDPE density 0.97 t/m3.
| 900mm diameter | metres | Plastic | 2.52 | tCO2e/t | 0.044662 | Carbon factor taken directly from the ICE V3: Plastic > HDPE Pipe. Conversion factor calculated from approximate 900mm pipe wall thickness of 16mm and HDPE density 0.97 t/m3.
| 1200mm diameter | metres | Plastic | 2.52 | tCO2e/t | 0.074355 | Carbon factor taken directly from the ICE V3: Plastic > HDPE Pipe. Conversion factor calculated from approximate 1200mm pipe wall thickness of 20mm and HDPE density of 0.97 t/m3.
| 1500mm diameter | metres | Plastic | 2.52 | tCO2e/t | 0.11618 | Carbon factor taken directly from the ICE V3: Plastic > HDPE Pipe. Conversion factor calculated from approximate 1500mm pipe wall thickness of 25mm and HDPE density of 0.97 t/m3.
| 1800mm diameter | metres | Plastic | 2.52 | tCO2e/t | 0.1673 | Carbon factor taken directly from the ICE V3: Plastic > HDPE Pipe. Conversion factor calculated from approximate 1800mm pipe wall thickness of 30mm and HDPE density of 0.97 t/m3.
Pump Power/Efficiency Formula
https://wilo.com/ie/en/Solutions-Finder/FAQ/Centrifugal-pump/What-is-the-efficiency-of-a-centrifugal-pump/

## Reference
Pump Selection:
Pump Max head (m) | Pump Max Flow rate capacity (m^3/s)
160 | 0.5
https://www.xylem.com/en-uk/products--services/pumps-packaged-pump-systems/pumps/end-suction-pumps/e-nsc-cast-iron-end-suction-pumps/
GPS Visualiser (google earth map converted to excel format)
PE100 Pipes are suitable for horizontal directional drilling installation
https://www.pe100plus.com/PE-Pipes/Technical-guidance/Trenchless/Methods/Installation/Horizontal-Directional-Drilling-i1305.html
Choose pump based on MAx pressure and required head, optimal pump is based on its highest efficiency for producing that required head
Pump 100m head
https://www.xylect.com/bin/Xylect.dll?RQID=C5306ABC8C4548B8B2C8E502AB5437E9
Pump 70m head
https://www.xylect.com/bin/Xylect.dll?RQID=C5306ABC8C4548B8B2C8E502AB5437E9
Pump 20m head
https://www.xylect.com/bin/Xylect.dll?RQID=58E15A6A4DFD4A4CAE3ECFAF96187650